## F4
Nume Proiect / Project Title:Proiectare Si Executie Lucrari Pentru Obiectivul De Investitii: Sediu Nou Pentru Spitalul De Urgenta Prof. Dr. Dimitrie Gerota
Numar Proiect / Project Number: 2S/2024
Data / Date: Septembrie 2025
Beneficiar / Beneficiary: Spitalul de Urgență ”Prof. Dr. Dimitrie Gerota”
Proiectant General / General Designer: Asocierea CCN ALTYAPI YATIRIMLARI VE INSAAT A.S. - CCN YATIRIM HOLDING A.S.
| LISTA ECHIPAMENTE | EQUIPMENT LIST
| LUCRARI DE INSTALATII SANITARE | SANITARY INSTALLATIONS WORKS
Nr. | Denumirea | Name | U.M. | Cantitate Quantity | Pret unitar (fara TVA) / Unit Price (without VAT) - Lei - | Valoarea (fara TVA) / Value (without VAT) - Lei - | Nr. Fisa tehnica | INDICATOR SCHEMA FUNCTIONALA | AMPLASARE / DETALII
0 | 1 | 1 | 2 | 3 | 4 | 5 = 3 X 4 | 6 | 7 | 8
Utilaje, echipamente tehnologice si functionale care necesita montaj / Cost of Machinery & equipment that requires assembly
8 | Statie clorinare, recirculare si tratare UV pentru rezerva hidranti - Cod schema F16 | Chlorination, water recirculation and UV Water Treatment Plant for hydrants water tank - Scheme code F16 | buc./pcs | 1 |  | 0 | Fisa tehnica nr 08 |  | subsol 3
9 | Statie clorinare, recirculare si tratare UV pentru rezerva sprinklere - Cod schema F17 | Chlorination, water recirculation and UV Water Treatment Plant for sprinkler water tank - Scheme code F17 | buc./pcs | 1 |  | 0 | Fisa tehnica nr 09 |  | subsol 3
15 | Statie dedurizare duplex pentru turnuri de racire - Cod schema W16 | Duplex type water softening unit for domestic water - Scheme code W16 | buc./pcs | 1 |  | 0 | Fisa tehnica nr 15 | W16
16 | Statie dedurizare duplex pentru apa dedurizata - Cod schema W12 | Duplex type water softening unit for softened water tank - Scheme code W12 | buc./pcs | 1 |  | 0 | Fisa tehnica nr 16 | W12
34 | Sterilizator UV apa rece potabila | UV sterilizer for potable cold water | buc./pcs | 1 |  | 0 | Fisa tehnica nr 34 |  | bazin put forat
35 | Filtru cu carbon activ tip duplex - Cod schema W25 | Duplex type activated carbon filter - Scheme code W25 | buc./pcs | 1 |  | 0 | Fisa tehnica nr 35 | W25
36 | Statie osmoza inversa - Cod schema W24 | Reverse osmosis unit - Scheme code W24 | buc./pcs | 1 |  | 0 | Fisa tehnica nr 36 | W24
37 | Sistem dozare substante dezinfectante pentru apa potabila | Dosing system for disinfectant substances for potable water | buc./pcs | 1 |  | 0 | Fisa tehnica nr 37 |  | rezervor apa put forat
38 | Sistem dozare substante floculante pentru apa de adaos instalatii HVAC | Dosing system for flocculant substances for HVAC systems makeup water | buc./pcs | 1 |  | 0 | Fisa tehnica nr 38 |  | turni racire
39 | Sistem dozare substante anti-alge pentru apa de adaos turnuri de racire | Dosing system for anti-algae substances for cooling towers makeup water | buc./pcs | 1 |  | 0 | Fisa tehnica nr 39 |  | turni racire
40 | Sistem dozare substante anti-coroziune si anti-depuneri pentru apa | Dosing system for anti-corrosion and anti-scaling substances for water | buc./pcs | 1 |  | 0 | Fisa tehnica nr 40 |  | bazin put forat
41 | Unitate de dozare pentru monocloramina | Dosing unit for monochloramine | buc./pcs | 2 |  | 0 | Fisa tehnica nr 41 |  | rezervor beton apa potabila
42 | Unitate de dozare pentru clor pentru sistem de recirculare bazine apa | Dosing unit for chlorine for recirculation system of potable water tanks | buc./pcs | 2 |  | 0 | Fisa tehnica nr 42 |  | rezervor beton apa potabila
59 | Filtru de nisip - Cod schema W26 | Sand filter - Scheme code W26 | buc./pcs | 1 |  | 0 | Fisa tehnica nr 59 | W26 | CAMERA TEHNICA S3
60 | Statie dedurizare duplex pentru puturile forate - Cod schema W34 | Duplex type water softening unit for well water - Scheme code W34 | buc./pcs | 1 |  | 0 | Fisa tehnica nr 60 | W34 | CAMERA TEHNICA S3
61 | Sistem dozare clor - Cod schema W36 | Chlorine dosing system - Scheme code W36 | buc./pcs | 1 |  | 0 | Fisa tehnica nr 61 | W36 | CAMERA TEHNICA S3
63 | Pompa recirculare bazin put forat - Cod schema W37 | Drilled well pool recirculation pump - Scheme code W37 | buc./pcs | 1 |  | 0 | Fisa tehnica nr 63 | W37 | CAMERA TEHNICA S3
71 | Filtru impuritati automat cu sita - Cod schema W35 | Automatic impurity filter with a screen - Scheme code W35 | buc./pcs | 1 |  | 0 | Fisa tehnica nr 71 | W35
TOTAL Utilaje, echipamente tehnologice si functionale care necesita montaj |  | TOTAL Cost of Machinery & equipment that requires assembly |  |  |  | 0
Utilaje, echipamente tehnologice si functionale care nu necesita montaj si echipamente de transport / Cost of Machinery & equipment that does not require assembly, and transport machinery
1
2
TOTAL Utilaje, echipamente tehnologice si functionale care nu necesita montaj si echipamente de transport |  | TOTAL Cost of Machinery & equipment that does not require assembly, and transport machinery |  |  |  | 0
Dotari / Furniture, Fixtures
1
2
TOTAL Dotari |  | TOTAL Furniture, Fixtures |  |  |  | 0
Active necorporale / Intangible assets
1
2
TOTAL Active necorporale |  | TOTAL Intangible assets |  |  |  | 0
TOTAL / TOTAL | [5 empty] | 0

## F5-08
Nume Proiect / Project Title:Proiectare Si Executie Lucrari Pentru Obiectivul De Investitii: Sediu Nou Pentru Spitalul De Urgenta Prof. Dr. Dimitrie Gerota
Numar Proiect / Project Number: 2S/2024
Data / Date: Septembrie 2025
Beneficiar / Beneficiary: Spitalul de Urgență ”Prof. Dr. Dimitrie Gerota”
Proiectant General / General Designer: Asocierea CCN ALTYAPI YATIRIMLARI VE INSAAT A.S. - CCN YATIRIM HOLDING A.S.
Formular F5: Fisele tehnice pentru echipamente, dotari |  | F5 Form: Technical sheet for equipments, furniture and fixtures
Nr. | Specificatii tehnice impuse prin caietul de sarcini | Technical specifications imposed by specification conditions - techincal notes | Corespondenta propunerii tehnice cu specificatiile tehnice impuse prin caietul de sarcini / Correspondence of the technical proposal with the technical specifications imposed by the specification conditions | Furnizor/Producator Provider/Manufacturer
0 | 1 | 1 | 2 | 3
Fisa tehnica nr. 08 Utilajul, echipamentul tehnologic: Statie clorinare si tratare UV pentru rezerva hidranti - Cod schema F16 |  | Technical sheet no. 08 Machinery, equipment: Chlorination and UV Water Treatment Plant for hydrants water tank - Scheme code F16
1 | Parametrii tehnici si functionali Statie de clorinare digitala, recirculare apa si tratare UV inclusiv pompa de dozare, pentru rezervorul de stingere incendiu hidranti Alimentare: 100 – 240V AC – 50/60Hz Putere consumată: 100W Presiune: 2 – 12 bar Debit: min. 15 mc/h Racord contor apă: 3/4 țol Capacitate rezervor clor: 120 litri Rezervorul va avea agrement de potabilitate | Technical and Functional Parameters Digital chlorination, water recirculation and UV treatment station, including dosing pump, for the fire-fighting water tank Power supply: 100 – 240 V AC, 50/60 Hz Power consumption: 100 W Pressure: 2 – 12 bar Flow rate: min. 15 m³/h Water meter connection: 3/4 inch Chlorine tank capacity: 120 liters Note: the tank will have potable water approval
2 | Specificatii de performanta si conditii privind siguranta in exploatare Echipamentele vor fi insotite de cartea tehnica, certificat de calitate si garantie | Performance specifications and operational safety conditions The equipment will be accompanied by the technical manual, certificate of quality, and warranty
3 | Conditii privind conformitatea cu standardele relevante Echipamentul va fi fabricat cf. normelor UE ISO 9001, ISO 14001. | Conditions regarding compliance with relevant standards The equipment shall be built in accordance with EU norms, ISO 9001, ISO 14001.
4 | Conditii de garantie si postgarantie Garantie: minim 2 ani de la punerea in functiune, orice inlocuire a echipamentului in timpul perioadei de garantie va duce la preluarea garantiei de catre echipamentul nou instalat. | Warranty and post-warranty conditions Warranty: minimum 2 years from the time of commissioning, any replacement of the equipment during the warranty period will lead to the warranty being taken over by the newly installed equipment.
5 | Conditii cu caracter tehnic Furnizorul de echipament va oferi: Asistenta tehnica pentru instalare si punere in functiune. Manual de instructiuni pentru instalare si operare. Certificat de calitate. Training gratuit pentru personalul facilitatii. Service gratuit pe perioada garantiei in atelierele autorizate de intretinere si service. | Technical conditions The equipment supplier will provide: - Technical assistance for installation and commissioning. - Installation and operating instructions manual. - Quality certificate. - Free training for the facility staff. - Free service during warranty in authorized maintenance and service workshops.

## F5-09
Nume Proiect / Project Title:Proiectare Si Executie Lucrari Pentru Obiectivul De Investitii: Sediu Nou Pentru Spitalul De Urgenta Prof. Dr. Dimitrie Gerota
Numar Proiect / Project Number: 2S/2024
Data / Date: Septembrie 2025
Beneficiar / Beneficiary: Spitalul de Urgență ”Prof. Dr. Dimitrie Gerota”
Proiectant General / General Designer: Asocierea CCN ALTYAPI YATIRIMLARI VE INSAAT A.S. - CCN YATIRIM HOLDING A.S.
Formular F5: Fisele tehnice pentru echipamente, dotari |  | F5 Form: Technical sheet for equipments, furniture and fixtures
Nr. | Specificatii tehnice impuse prin caietul de sarcini | Technical specifications imposed by specification conditions - techincal notes | Corespondenta propunerii tehnice cu specificatiile tehnice impuse prin caietul de sarcini / Correspondence of the technical proposal with the technical specifications imposed by the specification conditions | Furnizor/Producator Provider/Manufacturer
0 | 1 | 1 | 2 | 3
Fisa tehnica nr. 09 Utilajul, echipamentul tehnologic: Statie clorinare si tratare UV pentru rezerva sprinklere - Cod schema F17 |  | Technical sheet no. 09 Machinery, equipment: Chlorination and UV Water Treatment Plant for hydrants water tank - Scheme code F17
1 | Parametrii tehnici si functionali Statie de clorinare digitala, recirculare apa si tratare UV inclusiv pompa de dozare, pentru rezervorul de stingere incendiu sprinklere Alimentare: 100 – 240V AC – 50/60Hz Putere consumată: 100W Presiune: 2 – 12 bar Debit: min. 21 mc/h Racord contor apă: 3/4 țol Capacitate rezervor clor: 120 litri Rezervorul va avea agrement de potabilitate | Technical and Functional Parameters Digital chlorination, water recirculation and UV treatment station, including dosing pump, for the fire-fighting water tank Power supply: 100 – 240 V AC, 50/60 Hz Power consumption: 100 W Pressure: 2 – 12 bar Flow rate: min. 21 m³/h Water meter connection: 3/4 inch Chlorine tank capacity: 120 liters Note: the tank will have potable water approval
2 | Specificatii de performanta si conditii privind siguranta in exploatare Echipamentele vor fi insotite de cartea tehnica, certificat de calitate si garantie | Performance specifications and operational safety conditions The equipment will be accompanied by the technical manual, certificate of quality, and warranty
3 | Conditii privind conformitatea cu standardele relevante Echipamentul va fi fabricat cf. normelor UE ISO 9001, ISO 14001. | Conditions regarding compliance with relevant standards The equipment shall be built in accordance with EU norms, ISO 9001, ISO 14001.
4 | Conditii de garantie si postgarantie Garantie: minim 2 ani de la punerea in functiune, orice inlocuire a echipamentului in timpul perioadei de garantie va duce la preluarea garantiei de catre echipamentul nou instalat. | Warranty and post-warranty conditions Warranty: minimum 2 years from the time of commissioning, any replacement of the equipment during the warranty period will lead to the warranty being taken over by the newly installed equipment.
5 | Conditii cu caracter tehnic Furnizorul de echipament va oferi: Asistenta tehnica pentru instalare si punere in functiune. Manual de instructiuni pentru instalare si operare. Certificat de calitate. Training gratuit pentru personalul facilitatii. Service gratuit pe perioada garantiei in atelierele autorizate de intretinere si service. | Technical conditions The equipment supplier will provide: - Technical assistance for installation and commissioning. - Installation and operating instructions manual. - Quality certificate. - Free training for the facility staff. - Free service during warranty in authorized maintenance and service workshops.

## F5-15
Nume Proiect / Project Title:Proiectare Si Executie Lucrari Pentru Obiectivul De Investitii: Sediu Nou Pentru Spitalul De Urgenta Prof. Dr. Dimitrie Gerota
Numar Proiect / Project Number: 2S/2024
Data / Date: Septembrie 2025
Beneficiar / Beneficiary: Spitalul de Urgență ”Prof. Dr. Dimitrie Gerota”
Proiectant General / General Designer: Asocierea CCN ALTYAPI YATIRIMLARI VE INSAAT A.S. - CCN YATIRIM HOLDING A.S.
Formular F5: Fisele tehnice pentru echipamente, dotari |  | F5 Form: Technical sheet for equipments, furniture and fixtures
Nr. | Specificatii tehnice impuse prin caietul de sarcini | Technical specifications imposed by specification conditions - techincal notes | Corespondenta propunerii tehnice cu specificatiile tehnice impuse prin caietul de sarcini / Correspondence of the technical proposal with the technical specifications imposed by the specification conditions | Furnizor/Producator Provider/Manufacturer
0 | 1 | 1 | 2 | 3
Fisa tehnica nr. 15 Utilajul, echipamentul tehnologic: Statie dedurizare duplex pentru turnuri de racire - Cod schema W16 |  | Technical sheet no. 15 Machinery, equipment: Duplex type water softening unit for domestic water - Scheme code W16
1 | Parametrii tehnici si functionali Debit minim nominal: 50 mc/h. o Funcționare alternativă a rezervoarelor de rășină tip duplex o Regenerare controlată în funcție de volum o Supape sferice cu motor electric controlate prin PLC cu senzori de poziție finală o Doua coloane care vor functiona alternativ. - Poziționare flexibilă a rezervoarelor, a băii de sare și a suportului, după cum este necesar - Regenerare cu pat împachetat în contracurent pentru o capacitate sporită o Afișare și control al parametrilor sistemului o Ecran tactil și afișaj grafic o Structură standardizată a meniului o Opțional- conexiune Ethernet IP/TCP: Monitorizare la distanță - Afișare și control o Alarmă - Dozare precisă a saramurii datorită monitorizării conductivității - fără supradozare (consum de sare cu 60% mai mic în comparație cu dedurizatoarele tradiționale) - Design rezistent la coroziune - Presiune maxima: Pn16. | Technical and functional parameters Nominal flow rate: 50 cbm/h. o Alternate operation of duplex resin tanks o Volume-controlled regeneration o PLC controlled electric motor ball valves with end position sensors o Two columns which will operate alternately. - Flexible positioning of tanks, salt bath and skid as required - Packed bed countercurrent regenerated for increased capacity o Display and control of the system parameters o Touchscreen and graphics display o Standardized menu structure o Optional– IP/TCP Ethernet connection: Remote monitoring - Display and control o Alarm - Precision brine dosing thanks to conductivity monitoring – no overdosing (60% less salt consumption in comparison to traditional softeners) - Corrosion resistant design - Presiune maxima: Pn16.
2 | Specificatii de performanta si conditii privind siguranta in exploatare Echipamentele vor fi insotite de cartea tehnica, certificat de calitate si garantie | Performance specifications and operational safety conditions The equipment will be accompanied by the technical manual, certificate of quality, and warranty
3 | Conditii privind conformitatea cu standardele relevante Echipamentul va fi fabricat cf. normelor UE ISO 9001, ISO 14001. | Conditions regarding compliance with relevant standards The equipment shall be built in accordance with EU norms, ISO 9001, ISO 14001.
4 | Conditii de garantie si postgarantie Garantie: minim 2 ani de la punerea in functiune, orice inlocuire a echipamentului in timpul perioadei de garantie va duce la preluarea garantiei de catre echipamentul nou instalat. | Warranty and post-warranty conditions Warranty: minimum 2 years from the time of commissioning, any replacement of the equipment during the warranty period will lead to the warranty being taken over by the newly installed equipment.
5 | Conditii cu caracter tehnic Furnizorul de echipament va oferi: Asistenta tehnica pentru instalare si punere in functiune. Manual de instructiuni pentru instalare si operare. Certificat de calitate. Training gratuit pentru personalul facilitatii. Service gratuit pe perioada garantiei in atelierele autorizate de intretinere si service. | Technical conditions The equipment supplier will provide: - Technical assistance for installation and commissioning. - Installation and operating instructions manual. - Quality certificate. - Free training for the facility staff. - Free service during warranty in authorized maintenance and service workshops.

## F5-16
Nume Proiect / Project Title:Proiectare Si Executie Lucrari Pentru Obiectivul De Investitii: Sediu Nou Pentru Spitalul De Urgenta Prof. Dr. Dimitrie Gerota
Numar Proiect / Project Number: 2S/2024
Data / Date: Septembrie 2025
Beneficiar / Beneficiary: Spitalul de Urgență ”Prof. Dr. Dimitrie Gerota”
Proiectant General / General Designer: Asocierea CCN ALTYAPI YATIRIMLARI VE INSAAT A.S. - CCN YATIRIM HOLDING A.S.
Formular F5: Fisele tehnice pentru echipamente, dotari |  | F5 Form: Technical sheet for equipments, furniture and fixtures
Nr. | Specificatii tehnice impuse prin caietul de sarcini | Technical specifications imposed by specification conditions - techincal notes | Corespondenta propunerii tehnice cu specificatiile tehnice impuse prin caietul de sarcini / Correspondence of the technical proposal with the technical specifications imposed by the specification conditions | Furnizor/Producator Provider/Manufacturer
0 | 1 | 1 | 2 | 3
Fisa tehnica nr. 16 Utilajul, echipamentul tehnologic: Statie dedurizare duplex pentru apa dedurizata - Cod schema W12 |  | Technical sheet no. 16 Machinery, equipment: Duplex type water softening unit for softened water tank - Scheme code W12
1 | Parametrii tehnici si functionali Debit minim nominal: 15 mc/h. o Funcționare alternativă a rezervoarelor de rășină tip duplex o Regenerare controlată în funcție de volum o Supape sferice cu motor electric controlate prin PLC cu senzori de poziție finală o Doua coloane care vor functiona alternativ. - Poziționare flexibilă a rezervoarelor, a băii de sare și a suportului, după cum este necesar - Regenerare cu pat împachetat în contracurent pentru o capacitate sporită o Afișare și control al parametrilor sistemului o Ecran tactil și afișaj grafic o Structură standardizată a meniului o Opțional- conexiune Ethernet IP/TCP: Monitorizare la distanță - Afișare și control o Alarmă - Dozare precisă a saramurii datorită monitorizării conductivității - fără supradozare (consum de sare cu 60% mai mic în comparație cu dedurizatoarele tradiționale) - Design rezistent la coroziune - Presiune maxima: Pn16. | Technical and functional parameters Nominal flow rate: 15 cbm/h. o Alternate operation of duplex resin tanks o Volume-controlled regeneration o PLC controlled electric motor ball valves with end position sensors o Two columns which will operate alternately. - Flexible positioning of tanks, salt bath and skid as required - Packed bed countercurrent regenerated for increased capacity o Display and control of the system parameters o Touchscreen and graphics display o Standardized menu structure o Optional– IP/TCP Ethernet connection: Remote monitoring - Display and control o Alarm - Precision brine dosing thanks to conductivity monitoring – no overdosing (60% less salt consumption in comparison to traditional softeners) - Corrosion resistant design - Presiune maxima: Pn16.
2 | Specificatii de performanta si conditii privind siguranta in exploatare Echipamentele vor fi insotite de cartea tehnica, certificat de calitate si garantie | Performance specifications and operational safety conditions The equipment will be accompanied by the technical manual, certificate of quality, and warranty
3 | Conditii privind conformitatea cu standardele relevante Echipamentul va fi fabricat cf. normelor UE ISO 9001, ISO 14001. | Conditions regarding compliance with relevant standards The equipment shall be built in accordance with EU norms, ISO 9001, ISO 14001.
4 | Conditii de garantie si postgarantie Garantie: minim 2 ani de la punerea in functiune, orice inlocuire a echipamentului in timpul perioadei de garantie va duce la preluarea garantiei de catre echipamentul nou instalat. | Warranty and post-warranty conditions Warranty: minimum 2 years from the time of commissioning, any replacement of the equipment during the warranty period will lead to the warranty being taken over by the newly installed equipment.
5 | Conditii cu caracter tehnic Furnizorul de echipament va oferi: Asistenta tehnica pentru instalare si punere in functiune. Manual de instructiuni pentru instalare si operare. Certificat de calitate. Training gratuit pentru personalul facilitatii. Service gratuit pe perioada garantiei in atelierele autorizate de intretinere si service. | Technical conditions The equipment supplier will provide: - Technical assistance for installation and commissioning. - Installation and operating instructions manual. - Quality certificate. - Free training for the facility staff. - Free service during warranty in authorized maintenance and service workshops.

## F5-34
Nume Proiect / Project Title:Proiectare Si Executie Lucrari Pentru Obiectivul De Investitii: Sediu Nou Pentru Spitalul De Urgenta Prof. Dr. Dimitrie Gerota
Numar Proiect / Project Number: 2S/2024
Data / Date: Septembrie 2025
Beneficiar / Beneficiary: Spitalul de Urgență ”Prof. Dr. Dimitrie Gerota”
Proiectant General / General Designer: Asocierea CCN ALTYAPI YATIRIMLARI VE INSAAT A.S. - CCN YATIRIM HOLDING A.S.
Formular F5: Fisele tehnice pentru echipamente, dotari |  | F5 Form: Technical sheet for equipments, furniture and fixtures
Nr. | Specificatii tehnice impuse prin caietul de sarcini | Technical specifications imposed by specification conditions - techincal notes | Corespondenta propunerii tehnice cu specificatiile tehnice impuse prin caietul de sarcini / Correspondence of the technical proposal with the technical specifications imposed by the specification conditions | Furnizor/Producator Provider/Manufacturer
0 | 1 | 1 | 2 | 3
Fisa tehnica nr. 34 Utilajul, echipamentul tehnologic: Sterilizator UV apa rece potabila |  | Technical sheet no. 34 Machinery, equipment: UV sterilizer for potable cold water
1 | Parametrii tehnici si functionali - dezinfectare cu lampa cu ultraviolete - sistem cu posibilitate de curatare manual/automat - contoller local cu monitorizare continua a temperaturii, stari de alarma, eroare, ajustare parametri | Technical and functional parameters - disinfection with ultraviolete lamp - system with possibility of manual/automatic wipin - local contoller with continuous monitoring of temperature, faults, errors, parameter adjustment
2 | Specificatii de performanta si conditii privind siguranta in exploatare Echipamentele vor fi insotite de cartea tehnica, certificat de calitate si garantie | Performance specifications and operational safety conditions The equipment will be accompanied by the technical manual, certificate of quality, and warranty
3 | Conditii privind conformitatea cu standardele relevante Echipamentul va fi fabricat cf. normelor UE ISO 9001, ISO 14001. | Conditions regarding compliance with relevant standards The equipment shall be built in accordance with EU norms, ISO 9001, ISO 14001.
4 | Conditii de garantie si postgarantie Garantie: minim 2 ani de la punerea in functiune, orice inlocuire a echipamentului in timpul perioadei de garantie va duce la preluarea garantiei de catre echipamentul nou instalat. | Warranty and post-warranty conditions Warranty: minimum 2 years from the time of commissioning, any replacement of the equipment during the warranty period will lead to the warranty being taken over by the newly installed equipment.
5 | Conditii cu caracter tehnic Furnizorul de echipament va oferi: Asistenta tehnica pentru instalare si punere in functiune. Manual de instructiuni pentru instalare si operare. Certificat de calitate. Training gratuit pentru personalul facilitatii. Service gratuit pe perioada garantiei in atelierele autorizate de intretinere si service. | Technical conditions The equipment supplier will provide: - Technical assistance for installation and commissioning. - Installation and operating instructions manual. - Quality certificate. - Free training for the facility staff. - Free service during warranty in authorized maintenance and service workshops.

## F5-35
Nume Proiect / Project Title:Proiectare Si Executie Lucrari Pentru Obiectivul De Investitii: Sediu Nou Pentru Spitalul De Urgenta Prof. Dr. Dimitrie Gerota
Numar Proiect / Project Number: 2S/2024
Data / Date: Septembrie 2025
Beneficiar / Beneficiary: Spitalul de Urgență ”Prof. Dr. Dimitrie Gerota”
Proiectant General / General Designer: Asocierea CCN ALTYAPI YATIRIMLARI VE INSAAT A.S. - CCN YATIRIM HOLDING A.S.
Formular F5: Fisele tehnice pentru echipamente, dotari |  | F5 Form: Technical sheet for equipments, furniture and fixtures
Nr. | Specificatii tehnice impuse prin caietul de sarcini | Technical specifications imposed by specification conditions - techincal notes | Corespondenta propunerii tehnice cu specificatiile tehnice impuse prin caietul de sarcini / Correspondence of the technical proposal with the technical specifications imposed by the specification conditions | Furnizor/Producator Provider/Manufacturer
0 | 1 | 1 | 2 | 3
Fisa tehnica nr. 35 Utilajul, echipamentul tehnologic:Filtru cu carbon activ tip duplex - Cod schema W25 |  | Technical sheet no. 35 Machinery, equipment: Duplex type activated carbon filter - Scheme code W25
1 | Parametrii tehnici si functionali Debit minim nominal: 18 mc/h. Produs din material rezistent la coroziune cu durabilitate ridicată - Alimentare neîntreruptă cu apă proaspătă datorită filtrării duplex - Funcționare complet automată - supape electrice și transmițătoare de presiune - Spălare inversă automată - PLC de calitate industrială și panou tactil o Afișare și control al parametrilor sistemului o Ecran tactil și afișaj grafic o Structură standardizată a meniului o Conexiune Ethernet opțională: Monitorizare la distanță - Afișare și control o Alarmă - IP/TCP - Fabricat în UE - Alimentare neîntreruptă cu apă proaspătă datorită filtrării duplex - Funcționare complet automată - Spălare inversă automată Toata statie se va furniza complet de catre un producator de specialitate Echipamentele statiei de tratare vor fi stabilite in functie de parametrii din buletinul de analiza. | Technical and functional parameters Nominal flow rate: 18 cbm/h. Produced in corrosion resistant material with high durability - Uninterrupted Fresh Water supply thanks to Duplex Filtration - Fully automatic operation - Electrical valves and pressure transmitters - automatic backwash - Industrial grade PLC and touch panel o Display and control of the system parameters o Touchscreen and graphics Display o Standardized menu structure o Optional Ethernet connection: Remote monitoring - Display and control o Alarm – IP/TCP - Manufactured within the EU - Uninterrupted supply of fresh water thanks to duplex filtration - Fully automatic operation - Automatic backwash The whole station will be completely supplied by a specialized manufacturer The equipment of the treatment station will be established according to the parameters in the analysis bulletin.
2 | Specificatii de performanta si conditii privind siguranta in exploatare Echipamentele vor fi insotite de cartea tehnica, certificat de calitate si garantie | Performance specifications and operational safety conditions The equipment will be accompanied by the technical manual, certificate of quality, and warranty
3 | Conditii privind conformitatea cu standardele relevante Echipamentul va fi fabricat cf. normelor UE ISO 9001, ISO 14001. | Conditions regarding compliance with relevant standards The equipment shall be built in accordance with EU norms, ISO 9001, ISO 14001.
4 | Conditii de garantie si postgarantie Garantie: minim 2 ani de la punerea in functiune, orice inlocuire a echipamentului in timpul perioadei de garantie va duce la preluarea garantiei de catre echipamentul nou instalat. | Warranty and post-warranty conditions Warranty: minimum 2 years from the time of commissioning, any replacement of the equipment during the warranty period will lead to the warranty being taken over by the newly installed equipment.
5 | Conditii cu caracter tehnic Furnizorul de echipament va oferi: Asistenta tehnica pentru instalare si punere in functiune. Manual de instructiuni pentru instalare si operare. Certificat de calitate. Training gratuit pentru personalul facilitatii. Service gratuit pe perioada garantiei in atelierele autorizate de intretinere si service. | Technical conditions The equipment supplier will provide: - Technical assistance for installation and commissioning. - Installation and operating instructions manual. - Quality certificate. - Free training for the facility staff. - Free service during warranty in authorized maintenance and service workshops.

## F5-36
Nume Proiect / Project Title:Proiectare Si Executie Lucrari Pentru Obiectivul De Investitii: Sediu Nou Pentru Spitalul De Urgenta Prof. Dr. Dimitrie Gerota
Numar Proiect / Project Number: 2S/2024
Data / Date: Septembrie 2025
Beneficiar / Beneficiary: Spitalul de Urgență ”Prof. Dr. Dimitrie Gerota”
Proiectant General / General Designer: Asocierea CCN ALTYAPI YATIRIMLARI VE INSAAT A.S. - CCN YATIRIM HOLDING A.S.
Formular F5: Fisele tehnice pentru echipamente, dotari |  | F5 Form: Technical sheet for equipments, furniture and fixtures
Nr. | Specificatii tehnice impuse prin caietul de sarcini | Technical specifications imposed by specification conditions - techincal notes | Corespondenta propunerii tehnice cu specificatiile tehnice impuse prin caietul de sarcini / Correspondence of the technical proposal with the technical specifications imposed by the specification conditions | Furnizor/Producator Provider/Manufacturer
0 | 1 | 1 | 2 | 3
Fisa tehnica nr. 36 Utilajul, echipamentul tehnologic: Statie osmoza inversa - Cod schema W24 |  | Technical sheet no. 36 Machinery, equipment: Reverse osmosis unit - Scheme code W24
1 | Parametrii tehnici si functionali Debit minim nominal: 18 mc/h. - Instalare pe un cadru din oțel inoxidabil cu acces facil la toate componentele - Clătire automată la interval timp și calitate, pentru a asigura permeabilitatea și pentru a proteja membranele - Inclusiv sistem curățare eficientă a membranelor - Pompă de dozare anticalcar montată pe un suport - Pompă de rapel controlată în funcție de frecvență - asigură o funcționare fiabilă în zone cu presiuni și temperaturi fluctuante ale apei o Nivel ridicat de eficiență energetică și nivel redus de zgomot o Membrane de joasă presiune pentru economie de energie o Retenție de sare de până la 99,3 %. o Tuburi de presiune pentru schimbarea rapidă a membranelor Toata statie se va furniza complet de catre un producator de specialitate Echipamentele statiei de tratare vor fi stabilite in functie de parametrii din buletinul de analiza. | Technical and functional parameters Nominal flow rate: 18 cbm/h. - Installation on a stainless steel frame with optimum access to all components - Automated time and quality rinsing, to ensure permeability and to protect the membranes - Including effective cleaning of the membranes - Anti Scaling dosing pump skid mounted - Frequency-controled booster pump - ensures reliable operation in areas with fluctuating water pressures and temperatures o High energy efficiency level and low noice level o Energy-saving low-pressure membranes o Salt retention up to 99.3% o Pressure tubes for fast membrane changes The whole station will be completely supplied by a specialized manufacturer The equipment of the treatment station will be established according to the parameters in the analysis bulletin.
2 | Specificatii de performanta si conditii privind siguranta in exploatare Echipamentele vor fi insotite de cartea tehnica, certificat de calitate si garantie | Performance specifications and operational safety conditions The equipment will be accompanied by the technical manual, certificate of quality, and warranty
3 | Conditii privind conformitatea cu standardele relevante Echipamentul va fi fabricat cf. normelor UE ISO 9001, ISO 14001. | Conditions regarding compliance with relevant standards The equipment shall be built in accordance with EU norms, ISO 9001, ISO 14001.
4 | Conditii de garantie si postgarantie Garantie: minim 2 ani de la punerea in functiune, orice inlocuire a echipamentului in timpul perioadei de garantie va duce la preluarea garantiei de catre echipamentul nou instalat. | Warranty and post-warranty conditions Warranty: minimum 2 years from the time of commissioning, any replacement of the equipment during the warranty period will lead to the warranty being taken over by the newly installed equipment.
5 | Conditii cu caracter tehnic Furnizorul de echipament va oferi: Asistenta tehnica pentru instalare si punere in functiune. Manual de instructiuni pentru instalare si operare. Certificat de calitate. Training gratuit pentru personalul facilitatii. Service gratuit pe perioada garantiei in atelierele autorizate de intretinere si service. | Technical conditions The equipment supplier will provide: - Technical assistance for installation and commissioning. - Installation and operating instructions manual. - Quality certificate. - Free training for the facility staff. - Free service during warranty in authorized maintenance and service workshops.

## F5-37
Nume Proiect / Project Title:Proiectare Si Executie Lucrari Pentru Obiectivul De Investitii: Sediu Nou Pentru Spitalul De Urgenta Prof. Dr. Dimitrie Gerota
Numar Proiect / Project Number: 2S/2024
Data / Date: Septembrie 2025
Beneficiar / Beneficiary: Spitalul de Urgență ”Prof. Dr. Dimitrie Gerota”
Proiectant General / General Designer: Asocierea CCN ALTYAPI YATIRIMLARI VE INSAAT A.S. - CCN YATIRIM HOLDING A.S.
Formular F5: Fisele tehnice pentru echipamente, dotari |  | F5 Form: Technical sheet for equipments, furniture and fixtures
Nr. | Specificatii tehnice impuse prin caietul de sarcini | Technical specifications imposed by specification conditions - techincal notes | Corespondenta propunerii tehnice cu specificatiile tehnice impuse prin caietul de sarcini / Correspondence of the technical proposal with the technical specifications imposed by the specification conditions | Furnizor/Producator Provider/Manufacturer
0 | 1 | 1 | 2 | 3
Fisa tehnica nr. 37 Utilajul, echipamentul tehnologic: Sistem dozare substante dezinfectante pentru apa potabila |  | Technical sheet no. 37 Machinery, equipment: Dosing system for disinfectant substances for potable water
1 | Parametrii tehnici si functionali - Max. 40 l/h și 16 bar - Raport de reducere între 1:3000 și 1:1000 - FlowControl cu diagnosticare selectivă a defecțiunilor - Măsurare integrată a debitului - funcție care permite ajustarea vitezei pompei la cerinţele aplicaţiei - Dezaerare automată chiar și în timpul perioadei de repaus a pompei - Moduri de funcționare pe intervale (pe bază de cronometru sau de impulsuri) - ProfiBus opțional - Motor în trepte, puternic, cu viteză variabilă - Control intern al vitezei cursei - Cursă completă în permanență - chiar și la debite mici - Dozare lină și continuă - Optim pentru degazarea lichidelor - Funcție pentru lichide cu vâscozitate ridicată | Technical and functional parameters - Max. 40 l/h and 16 bar - Turn-down ratio 1:3000 or 1:1000 - FlowControl with selective fault diagnosis - Integrated flow measurement - function that allows adjusting the pump speed to the requirements of the application - Auto deaeration also during pump standby - Batch modes (timer- or pulse-based) - Optional Profibus - Powerful variable-speed stepper motor - Internal stroke speed control - Always full stroke length – even at small flow rates - Smooth, continuous dosing - Optimal for degassing liquids - Function for high-viscosity liquids
2 | Specificatii de performanta si conditii privind siguranta in exploatare Echipamentele vor fi insotite de cartea tehnica, certificat de calitate si garantie | Performance specifications and operational safety conditions The equipment will be accompanied by the technical manual, certificate of quality, and warranty
3 | Conditii privind conformitatea cu standardele relevante Echipamentul va fi fabricat cf. normelor UE ISO 9001, ISO 14001. | Conditions regarding compliance with relevant standards The equipment shall be built in accordance with EU norms, ISO 9001, ISO 14001.
4 | Conditii de garantie si postgarantie Garantie: minim 2 ani de la punerea in functiune, orice inlocuire a echipamentului in timpul perioadei de garantie va duce la preluarea garantiei de catre echipamentul nou instalat. | Warranty and post-warranty conditions Warranty: minimum 2 years from the time of commissioning, any replacement of the equipment during the warranty period will lead to the warranty being taken over by the newly installed equipment.
5 | Conditii cu caracter tehnic Furnizorul de echipament va oferi: Asistenta tehnica pentru instalare si punere in functiune. Manual de instructiuni pentru instalare si operare. Certificat de calitate. Training gratuit pentru personalul facilitatii. Service gratuit pe perioada garantiei in atelierele autorizate de intretinere si service. | Technical conditions The equipment supplier will provide: - Technical assistance for installation and commissioning. - Installation and operating instructions manual. - Quality certificate. - Free training for the facility staff. - Free service during warranty in authorized maintenance and service workshops.

## F5-38
Nume Proiect / Project Title:Proiectare Si Executie Lucrari Pentru Obiectivul De Investitii: Sediu Nou Pentru Spitalul De Urgenta Prof. Dr. Dimitrie Gerota
Numar Proiect / Project Number: 2S/2024
Data / Date: Septembrie 2025
Beneficiar / Beneficiary: Spitalul de Urgență ”Prof. Dr. Dimitrie Gerota”
Proiectant General / General Designer: Asocierea CCN ALTYAPI YATIRIMLARI VE INSAAT A.S. - CCN YATIRIM HOLDING A.S.
Formular F5: Fisele tehnice pentru echipamente, dotari |  | F5 Form: Technical sheet for equipments, furniture and fixtures
Nr. | Specificatii tehnice impuse prin caietul de sarcini | Technical specifications imposed by specification conditions - techincal notes | Corespondenta propunerii tehnice cu specificatiile tehnice impuse prin caietul de sarcini / Correspondence of the technical proposal with the technical specifications imposed by the specification conditions | Furnizor/Producator Provider/Manufacturer
0 | 1 | 1 | 2 | 3
Fisa tehnica nr. 38 Utilajul, echipamentul tehnologic: Sistem dozare substante floculante pentru apa de adaos instalatii HVAC |  | Technical sheet no. 38 Machinery, equipment: Dosing system for flocculant substances for HVAC systems makeup water
1 | Parametrii tehnici si functionali - Max. 40 l/h și 16 bar - Raport de reducere între 1:3000 și 1:1000 - FlowControl cu diagnosticare selectivă a defecțiunilor - Măsurare integrată a debitului - funcție care permite ajustarea vitezei pompei la cerinţele aplicaţiei - Dezaerare automată chiar și în timpul perioadei de repaus a pompei - Moduri de funcționare pe intervale (pe bază de cronometru sau de impulsuri) - ProfiBus opțional - Motor în trepte, puternic, cu viteză variabilă - Control intern al vitezei cursei - Cursă completă în permanență - chiar și la debite mici - Dozare lină și continuă - Optim pentru degazarea lichidelor - Funcție pentru lichide cu vâscozitate ridicată | Technical and functional parameters - Max. 40 l/h and 16 bar - Turn-down ratio 1:3000 (7.5-16) or 1:1000 - FlowControl with selective fault diagnosis - Integrated flow measurement - function that allows adjusting the pump speed to the requirements of the application - Auto deaeration also during pump standby - Batch modes (timer- or pulse-based) - Optional Profibus - Powerful variable-speed stepper motor - Internal stroke speed control - Always full stroke length – even at small flow rates - Smooth, continuous dosing - Optimal for degassing liquids - function for high-viscosity liquids
2 | Specificatii de performanta si conditii privind siguranta in exploatare Echipamentele vor fi insotite de cartea tehnica, certificat de calitate si garantie | Performance specifications and operational safety conditions The equipment will be accompanied by the technical manual, certificate of quality, and warranty
3 | Conditii privind conformitatea cu standardele relevante Echipamentul va fi fabricat cf. normelor UE ISO 9001, ISO 14001. | Conditions regarding compliance with relevant standards The equipment shall be built in accordance with EU norms, ISO 9001, ISO 14001.
4 | Conditii de garantie si postgarantie Garantie: minim 2 ani de la punerea in functiune, orice inlocuire a echipamentului in timpul perioadei de garantie va duce la preluarea garantiei de catre echipamentul nou instalat. | Warranty and post-warranty conditions Warranty: minimum 2 years from the time of commissioning, any replacement of the equipment during the warranty period will lead to the warranty being taken over by the newly installed equipment.
5 | Conditii cu caracter tehnic Furnizorul de echipament va oferi: Asistenta tehnica pentru instalare si punere in functiune. Manual de instructiuni pentru instalare si operare. Certificat de calitate. Training gratuit pentru personalul facilitatii. Service gratuit pe perioada garantiei in atelierele autorizate de intretinere si service. | Technical conditions The equipment supplier will provide: - Technical assistance for installation and commissioning. - Installation and operating instructions manual. - Quality certificate. - Free training for the facility staff. - Free service during warranty in authorized maintenance and service workshops.

## F5-39
Nume Proiect / Project Title:Proiectare Si Executie Lucrari Pentru Obiectivul De Investitii: Sediu Nou Pentru Spitalul De Urgenta Prof. Dr. Dimitrie Gerota
Numar Proiect / Project Number: 2S/2024
Data / Date: Septembrie 2025
Beneficiar / Beneficiary: Spitalul de Urgență ”Prof. Dr. Dimitrie Gerota”
Proiectant General / General Designer: Asocierea CCN ALTYAPI YATIRIMLARI VE INSAAT A.S. - CCN YATIRIM HOLDING A.S.
Formular F5: Fisele tehnice pentru echipamente, dotari |  | F5 Form: Technical sheet for equipments, furniture and fixtures
Nr. | Specificatii tehnice impuse prin caietul de sarcini | Technical specifications imposed by specification conditions - techincal notes | Corespondenta propunerii tehnice cu specificatiile tehnice impuse prin caietul de sarcini / Correspondence of the technical proposal with the technical specifications imposed by the specification conditions | Furnizor/Producator Provider/Manufacturer
0 | 1 | 1 | 2 | 3
Fisa tehnica nr. 39 Utilajul, echipamentul tehnologic: Sistem dozare substante anti-alge pentru apa de adaos turnuri de racire |  | Technical sheet no. 39 Machinery, equipment: Dosing system for anti-algae substances for cooling towers makeup water
1 | Parametrii tehnici si functionali - Max. 40 l/h și 16 bar - Raport de reducere între 1:3000 și 1:1000 - FlowControl cu diagnosticare selectivă a defecțiunilor - Măsurare integrată a debitului - funcție care permite ajustarea vitezei pompei la cerinţele aplicaţiei - Dezaerare automată chiar și în timpul perioadei de repaus a pompei - Moduri de funcționare pe intervale (pe bază de cronometru sau de impulsuri) - ProfiBus opțional - Motor în trepte, puternic, cu viteză variabilă - Control intern al vitezei cursei - Cursă completă în permanență - chiar și la debite mici - Dozare lină și continuă - Optim pentru degazarea lichidelor - Funcție pentru lichide cu vâscozitate ridicată | Technical and functional parameters - Max. 40 l/h and 16 bar - Turn-down ratio 1:3000 (7.5-16) or 1:1000 - FlowControl with selective fault diagnosis - Integrated flow measurement - function that allows adjusting the pump speed to the requirements of the application - Auto deaeration also during pump standby - Batch modes (timer- or pulse-based) - Optional Profibus - Powerful variable-speed stepper motor - Internal stroke speed control - Always full stroke length – even at small flow rates - Smooth, continuous dosing - Optimal for degassing liquids - function for high-viscosity liquids
2 | Specificatii de performanta si conditii privind siguranta in exploatare Echipamentele vor fi insotite de cartea tehnica, certificat de calitate si garantie | Performance specifications and operational safety conditions The equipment will be accompanied by the technical manual, certificate of quality, and warranty
3 | Conditii privind conformitatea cu standardele relevante Echipamentul va fi fabricat cf. normelor UE ISO 9001, ISO 14001. | Conditions regarding compliance with relevant standards The equipment shall be built in accordance with EU norms, ISO 9001, ISO 14001.
4 | Conditii de garantie si postgarantie Garantie: minim 2 ani de la punerea in functiune, orice inlocuire a echipamentului in timpul perioadei de garantie va duce la preluarea garantiei de catre echipamentul nou instalat. | Warranty and post-warranty conditions Warranty: minimum 2 years from the time of commissioning, any replacement of the equipment during the warranty period will lead to the warranty being taken over by the newly installed equipment.
5 | Conditii cu caracter tehnic Furnizorul de echipament va oferi: Asistenta tehnica pentru instalare si punere in functiune. Manual de instructiuni pentru instalare si operare. Certificat de calitate. Training gratuit pentru personalul facilitatii. Service gratuit pe perioada garantiei in atelierele autorizate de intretinere si service. | Technical conditions The equipment supplier will provide: - Technical assistance for installation and commissioning. - Installation and operating instructions manual. - Quality certificate. - Free training for the facility staff. - Free service during warranty in authorized maintenance and service workshops.

## F5-40
Nume Proiect / Project Title:Proiectare Si Executie Lucrari Pentru Obiectivul De Investitii: Sediu Nou Pentru Spitalul De Urgenta Prof. Dr. Dimitrie Gerota
Numar Proiect / Project Number: 2S/2024
Data / Date: Septembrie 2025
Beneficiar / Beneficiary: Spitalul de Urgență ”Prof. Dr. Dimitrie Gerota”
Proiectant General / General Designer: Asocierea CCN ALTYAPI YATIRIMLARI VE INSAAT A.S. - CCN YATIRIM HOLDING A.S.
Formular F5: Fisele tehnice pentru echipamente, dotari |  | F5 Form: Technical sheet for equipments, furniture and fixtures
Nr. | Specificatii tehnice impuse prin caietul de sarcini | Technical specifications imposed by specification conditions - techincal notes | Corespondenta propunerii tehnice cu specificatiile tehnice impuse prin caietul de sarcini / Correspondence of the technical proposal with the technical specifications imposed by the specification conditions | Furnizor/Producator Provider/Manufacturer
0 | 1 | 1 | 2 | 3
Fisa tehnica nr. 40 Utilajul, echipamentul tehnologic: Sistem dozare substante anti-coroziune si anti-depuneri pentru apa |  | Technical sheet no. 40 Machinery, equipment: Dosing system for anti-corrosion and anti-scaling substances for water
1 | Parametrii tehnici si functionali - Max. 40 l/h și 16 bar - Raport de reducere între 1:3000 și 1:1000 - FlowControl cu diagnosticare selectivă a defecțiunilor - Măsurare integrată a debitului - funcție care permite ajustarea vitezei pompei la cerinţele aplicaţiei - Dezaerare automată chiar și în timpul perioadei de repaus a pompei - Moduri de funcționare pe intervale (pe bază de cronometru sau de impulsuri) - ProfiBus opțional - Motor în trepte, puternic, cu viteză variabilă - Control intern al vitezei cursei - Cursă completă în permanență - chiar și la debite mici - Dozare lină și continuă - Optim pentru degazarea lichidelor - Funcție pentru lichide cu vâscozitate ridicată | Technical and functional parameters - Max. 40 l/h and 16 bar - Turn-down ratio 1:3000 (7.5-16) or 1:1000 - FlowControl with selective fault diagnosis - Integrated flow measurement - function that allows adjusting the pump speed to the requirements of the application - Auto deaeration also during pump standby - Batch modes (timer- or pulse-based) - Optional Profibus - Powerful variable-speed stepper motor - Internal stroke speed control - Always full stroke length – even at small flow rates - Smooth, continuous dosing - Optimal for degassing liquids - function for high-viscosity liquids
2 | Specificatii de performanta si conditii privind siguranta in exploatare Echipamentele vor fi insotite de cartea tehnica, certificat de calitate si garantie | Performance specifications and operational safety conditions The equipment will be accompanied by the technical manual, certificate of quality, and warranty
3 | Conditii privind conformitatea cu standardele relevante Echipamentul va fi fabricat cf. normelor UE ISO 9001, ISO 14001. | Conditions regarding compliance with relevant standards The equipment shall be built in accordance with EU norms, ISO 9001, ISO 14001.
4 | Conditii de garantie si postgarantie Garantie: minim 2 ani de la punerea in functiune, orice inlocuire a echipamentului in timpul perioadei de garantie va duce la preluarea garantiei de catre echipamentul nou instalat. | Warranty and post-warranty conditions Warranty: minimum 2 years from the time of commissioning, any replacement of the equipment during the warranty period will lead to the warranty being taken over by the newly installed equipment.
5 | Conditii cu caracter tehnic Furnizorul de echipament va oferi: Asistenta tehnica pentru instalare si punere in functiune. Manual de instructiuni pentru instalare si operare. Certificat de calitate. Training gratuit pentru personalul facilitatii. Service gratuit pe perioada garantiei in atelierele autorizate de intretinere si service. | Technical conditions The equipment supplier will provide: - Technical assistance for installation and commissioning. - Installation and operating instructions manual. - Quality certificate. - Free training for the facility staff. - Free service during warranty in authorized maintenance and service workshops.

## F5-41
Nume Proiect / Project Title:Proiectare Si Executie Lucrari Pentru Obiectivul De Investitii: Sediu Nou Pentru Spitalul De Urgenta Prof. Dr. Dimitrie Gerota
Numar Proiect / Project Number: 2S/2024
Data / Date: Septembrie 2025
Beneficiar / Beneficiary: Spitalul de Urgență ”Prof. Dr. Dimitrie Gerota”
Proiectant General / General Designer: Asocierea CCN ALTYAPI YATIRIMLARI VE INSAAT A.S. - CCN YATIRIM HOLDING A.S.
Formular F5: Fisele tehnice pentru echipamente, dotari |  | F5 Form: Technical sheet for equipments, furniture and fixtures
Nr. | Specificatii tehnice impuse prin caietul de sarcini | Technical specifications imposed by specification conditions - techincal notes | Corespondenta propunerii tehnice cu specificatiile tehnice impuse prin caietul de sarcini / Correspondence of the technical proposal with the technical specifications imposed by the specification conditions | Furnizor/Producator Provider/Manufacturer
0 | 1 | 1 | 2 | 3
Fisa tehnica nr. 41 Utilajul, echipamentul tehnologic: Unitate de dozare pentru monocloramina |  | Technical sheet no. 41 Machinery, equipment: Dosing unit for monochloramine
1 | Parametrii tehnici si functionali - Max. 40 l/h și 16 bar - Raport de reducere între 1:3000 și 1:1000 - FlowControl cu diagnosticare selectivă a defecțiunilor - Măsurare integrată a debitului - funcție care permite ajustarea vitezei pompei la cerinţele aplicaţiei - Dezaerare automată chiar și în timpul perioadei de repaus a pompei - Moduri de funcționare pe intervale (pe bază de cronometru sau de impulsuri) - ProfiBus opțional - Motor în trepte, puternic, cu viteză variabilă - Control intern al vitezei cursei - Cursă completă în permanență - chiar și la debite mici - Dozare lină și continuă - Optim pentru degazarea lichidelor - Funcție pentru lichide cu vâscozitate ridicată | Technical and functional parameters - Max. 40 l/h and 16 bar - Turn-down ratio 1:3000 (7.5-16) or 1:1000 - FlowControl with selective fault diagnosis - Integrated flow measurement - function that allows adjusting the pump speed to the requirements of the application - Auto deaeration also during pump standby - Batch modes (timer- or pulse-based) - Optional Profibus - Powerful variable-speed stepper motor - Internal stroke speed control - Always full stroke length – even at small flow rates - Smooth, continuous dosing - Optimal for degassing liquids - Function for high-viscosity liquids
2 | Specificatii de performanta si conditii privind siguranta in exploatare Echipamentele vor fi insotite de cartea tehnica, certificat de calitate si garantie | Performance specifications and operational safety conditions The equipment will be accompanied by the technical manual, certificate of quality, and warranty
3 | Conditii privind conformitatea cu standardele relevante Echipamentul va fi fabricat cf. normelor UE ISO 9001, ISO 14001. | Conditions regarding compliance with relevant standards The equipment shall be built in accordance with EU norms, ISO 9001, ISO 14001.
4 | Conditii de garantie si postgarantie Garantie: minim 2 ani de la punerea in functiune, orice inlocuire a echipamentului in timpul perioadei de garantie va duce la preluarea garantiei de catre echipamentul nou instalat. | Warranty and post-warranty conditions Warranty: minimum 2 years from the time of commissioning, any replacement of the equipment during the warranty period will lead to the warranty being taken over by the newly installed equipment.
5 | Conditii cu caracter tehnic Furnizorul de echipament va oferi: Asistenta tehnica pentru instalare si punere in functiune. Manual de instructiuni pentru instalare si operare. Certificat de calitate. Training gratuit pentru personalul facilitatii. Service gratuit pe perioada garantiei in atelierele autorizate de intretinere si service. | Technical conditions The equipment supplier will provide: - Technical assistance for installation and commissioning. - Installation and operating instructions manual. - Quality certificate. - Free training for the facility staff. - Free service during warranty in authorized maintenance and service workshops.

## F5-42
Nume Proiect / Project Title:Proiectare Si Executie Lucrari Pentru Obiectivul De Investitii: Sediu Nou Pentru Spitalul De Urgenta Prof. Dr. Dimitrie Gerota
Numar Proiect / Project Number: 2S/2024
Data / Date: Septembrie 2025
Beneficiar / Beneficiary: Spitalul de Urgență ”Prof. Dr. Dimitrie Gerota”
Proiectant General / General Designer: Asocierea CCN ALTYAPI YATIRIMLARI VE INSAAT A.S. - CCN YATIRIM HOLDING A.S.
Formular F5: Fisele tehnice pentru echipamente, dotari |  | F5 Form: Technical sheet for equipments, furniture and fixtures
Nr. | Specificatii tehnice impuse prin caietul de sarcini | Technical specifications imposed by specification conditions - techincal notes | Corespondenta propunerii tehnice cu specificatiile tehnice impuse prin caietul de sarcini / Correspondence of the technical proposal with the technical specifications imposed by the specification conditions | Furnizor/Producator Provider/Manufacturer
0 | 1 | 1 | 2 | 3
Fisa tehnica nr. 42 Utilajul, echipamentul tehnologic: Unitate de dozare pentru clor pentru sistem de recirculare bazine apa |  | Technical sheet no. 42 Machinery, equipment: Dosing unit for chlorine for recirculation system of potable water tanks
1 | Parametrii tehnici si functionali - Max. 40 l/h și 16 bar - Raport de reducere între 1:3000 și 1:1000 - FlowControl cu diagnosticare selectivă a defecțiunilor - Măsurare integrată a debitului - funcție care permite ajustarea vitezei pompei la cerinţele aplicaţiei - Dezaerare automată chiar și în timpul perioadei de repaus a pompei - Moduri de funcționare pe intervale (pe bază de cronometru sau de impulsuri) - ProfiBus opțional - Motor în trepte, puternic, cu viteză variabilă - Control intern al vitezei cursei - Cursă completă în permanență - chiar și la debite mici - Dozare lină și continuă - Optim pentru degazarea lichidelor - Funcție pentru lichide cu vâscozitate ridicată | Technical and functional parameters - Max. 40 l/h and 16 bar - Turn-down ratio 1:3000 (7.5-16) or 1:1000 - FlowControl with selective fault diagnosis - Integrated flow measurement - function that allows adjusting the pump speed to the requirements of the application - Auto deaeration also during pump standby - Batch modes (timer- or pulse-based) - Optional Profibus - Powerful variable-speed stepper motor - Internal stroke speed control - Always full stroke length – even at small flow rates - Smooth, continuous dosing - Optimal for degassing liquids - Function for high-viscosity liquids
2 | Specificatii de performanta si conditii privind siguranta in exploatare Echipamentele vor fi insotite de cartea tehnica, certificat de calitate si garantie | Performance specifications and operational safety conditions The equipment will be accompanied by the technical manual, certificate of quality, and warranty
3 | Conditii privind conformitatea cu standardele relevante Echipamentul va fi fabricat cf. normelor UE ISO 9001, ISO 14001. | Conditions regarding compliance with relevant standards The equipment shall be built in accordance with EU norms, ISO 9001, ISO 14001.
4 | Conditii de garantie si postgarantie Garantie: minim 2 ani de la punerea in functiune, orice inlocuire a echipamentului in timpul perioadei de garantie va duce la preluarea garantiei de catre echipamentul nou instalat. | Warranty and post-warranty conditions Warranty: minimum 2 years from the time of commissioning, any replacement of the equipment during the warranty period will lead to the warranty being taken over by the newly installed equipment.
5 | Conditii cu caracter tehnic Furnizorul de echipament va oferi: Asistenta tehnica pentru instalare si punere in functiune. Manual de instructiuni pentru instalare si operare. Certificat de calitate. Training gratuit pentru personalul facilitatii. Service gratuit pe perioada garantiei in atelierele autorizate de intretinere si service. | Technical conditions The equipment supplier will provide: - Technical assistance for installation and commissioning. - Installation and operating instructions manual. - Quality certificate. - Free training for the facility staff. - Free service during warranty in authorized maintenance and service workshops.

## F5-59
Nume Proiect / Project Title:Proiectare Si Executie Lucrari Pentru Obiectivul De Investitii: Sediu Nou Pentru Spitalul De Urgenta Prof. Dr. Dimitrie Gerota
Numar Proiect / Project Number: 2S/2024
Data / Date: Septembrie 2025
Beneficiar / Beneficiary: Spitalul de Urgență ”Prof. Dr. Dimitrie Gerota”
Proiectant General / General Designer: Asocierea CCN ALTYAPI YATIRIMLARI VE INSAAT A.S. - CCN YATIRIM HOLDING A.S.
Formular F5: Fisele tehnice pentru echipamente, dotari |  | F5 Form: Technical sheet for equipments, furniture and fixtures
Nr. | Specificatii tehnice impuse prin caietul de sarcini | Technical specifications imposed by specification conditions - techincal notes | Corespondenta propunerii tehnice cu specificatiile tehnice impuse prin caietul de sarcini / Correspondence of the technical proposal with the technical specifications imposed by the specification conditions | Furnizor/Producator Provider/Manufacturer
0 | 1 | 1 | 2 | 3
Fisa tehnica nr. 59 Utilajul, echipamentul tehnologic: Filtru de nisip - Cod schema W26 |  | Technical sheet no. 59 Machinery, equipment: Sand filter - Scheme code W26
1 | Parametrii tehnici si functionali Debit minim nominal: 18 mc/h. Inaltime totala: 1100mm Diametru exterior: 610mm Greutate: 44kg Capacitate maxima nisip: 200kg Toata statie se va furniza complet de catre un producator de specialitate Echipamentele statiei de tratare vor fi stabilite in functie de parametrii din buletinul de analiza. | Technical and functional parameters Nominal flow rate: 18 cbm/h. Overall height: 1100mm Outer diameter: 610mm Weight: 44kg Maximum sand capacity: 200kg The whole station will be completely supplied by a specialized manufacturer The equipment of the treatment station will be established according to the parameters in the analysis bulletin.
2 | Specificatii de performanta si conditii privind siguranta in exploatare Echipamentele vor fi insotite de cartea tehnica, certificat de calitate si garantie | Performance specifications and operational safety conditions The equipment will be accompanied by the technical manual, certificate of quality, and warranty
3 | Conditii privind conformitatea cu standardele relevante Echipamentul va fi fabricat cf. normelor UE ISO 9001, ISO 14001. | Conditions regarding compliance with relevant standards The equipment shall be built in accordance with EU norms, ISO 9001, ISO 14001.
4 | Conditii de garantie si postgarantie Garantie: minim 2 ani de la punerea in functiune, orice inlocuire a echipamentului in timpul perioadei de garantie va duce la preluarea garantiei de catre echipamentul nou instalat. | Warranty and post-warranty conditions Warranty: minimum 2 years from the time of commissioning, any replacement of the equipment during the warranty period will lead to the warranty being taken over by the newly installed equipment.
5 | Conditii cu caracter tehnic Furnizorul de echipament va oferi: Asistenta tehnica pentru instalare si punere in functiune. Manual de instructiuni pentru instalare si operare. Certificat de calitate. Training gratuit pentru personalul facilitatii. Service gratuit pe perioada garantiei in atelierele autorizate de intretinere si service. | Technical conditions The equipment supplier will provide: - Technical assistance for installation and commissioning. - Installation and operating instructions manual. - Quality certificate. - Free training for the facility staff. - Free service during warranty in authorized maintenance and service workshops.

## F5-60
Nume Proiect / Project Title:Proiectare Si Executie Lucrari Pentru Obiectivul De Investitii: Sediu Nou Pentru Spitalul De Urgenta Prof. Dr. Dimitrie Gerota
Numar Proiect / Project Number: 2S/2024
Data / Date: Septembrie 2025
Beneficiar / Beneficiary: Spitalul de Urgență ”Prof. Dr. Dimitrie Gerota”
Proiectant General / General Designer: Asocierea CCN ALTYAPI YATIRIMLARI VE INSAAT A.S. - CCN YATIRIM HOLDING A.S.
Formular F5: Fisele tehnice pentru echipamente, dotari |  | F5 Form: Technical sheet for equipments, furniture and fixtures
Nr. | Specificatii tehnice impuse prin caietul de sarcini | Technical specifications imposed by specification conditions - techincal notes | Corespondenta propunerii tehnice cu specificatiile tehnice impuse prin caietul de sarcini / Correspondence of the technical proposal with the technical specifications imposed by the specification conditions | Furnizor/Producator Provider/Manufacturer
0 | 1 | 1 | 2 | 3
Fisa tehnica nr. 60 Utilajul, echipamentul tehnologic: Statie dedurizare duplex pentru puturile forate - Cod schema W34 |  | Technical sheet no. 60 Machinery, equipment: Duplex type water softening unit for well water - Scheme code W34
1 | Parametrii tehnici si functionali Debit minim nominal: 18 mc/h. o Funcționare alternativă a rezervoarelor de rășină tip duplex o Regenerare controlată în funcție de volum o Supape sferice cu motor electric controlate prin PLC cu senzori de poziție finală o Doua coloane care vor functiona alternativ. - Poziționare flexibilă a rezervoarelor, a băii de sare și a suportului, după cum este necesar - Regenerare cu pat împachetat în contracurent pentru o capacitate sporită o Afișare și control al parametrilor sistemului o Ecran tactil și afișaj grafic o Structură standardizată a meniului o Opțional- conexiune Ethernet IP/TCP: Monitorizare la distanță - Afișare și control o Alarmă - Dozare precisă a saramurii datorită monitorizării conductivității - fără supradozare (consum de sare cu 60% mai mic în comparație cu dedurizatoarele tradiționale) - Design rezistent la coroziune Toata statie se va furniza complet de catre un producator de specialitate Echipamentele statiei de tratare vor fi stabilite in functie de parametrii din buletinul de analiza. | Technical and functional parameters Nominal flow rate: 18 cbm/h. o Alternate operation of duplex resin tanks o Volume-controlled regeneration o PLC controlled electric motor ball valves with end position sensors o Two columns which will operate alternately. - Flexible positioning of tanks, salt bath and skid as required - Packed bed countercurrent regenerated for increased capacity o Display and control of the system parameters o Touchscreen and graphics display o Standardized menu structure o Optional– IP/TCP Ethernet connection: Remote monitoring - Display and control o Alarm - Precision brine dosing thanks to conductivity monitoring – no overdosing (60% less salt consumption in comparison to traditional softeners) - Corrosion resistant design The whole station will be completely supplied by a specialized manufacturer The equipment of the treatment station will be established according to the parameters in the analysis bulletin.
2 | Specificatii de performanta si conditii privind siguranta in exploatare Echipamentele vor fi insotite de cartea tehnica, certificat de calitate si garantie | Performance specifications and operational safety conditions The equipment will be accompanied by the technical manual, certificate of quality, and warranty
3 | Conditii privind conformitatea cu standardele relevante Echipamentul va fi fabricat cf. normelor UE ISO 9001, ISO 14001. | Conditions regarding compliance with relevant standards The equipment shall be built in accordance with EU norms, ISO 9001, ISO 14001.
4 | Conditii de garantie si postgarantie Garantie: minim 2 ani de la punerea in functiune, orice inlocuire a echipamentului in timpul perioadei de garantie va duce la preluarea garantiei de catre echipamentul nou instalat. | Warranty and post-warranty conditions Warranty: minimum 2 years from the time of commissioning, any replacement of the equipment during the warranty period will lead to the warranty being taken over by the newly installed equipment.
5 | Conditii cu caracter tehnic Furnizorul de echipament va oferi: Asistenta tehnica pentru instalare si punere in functiune. Manual de instructiuni pentru instalare si operare. Certificat de calitate. Training gratuit pentru personalul facilitatii. Service gratuit pe perioada garantiei in atelierele autorizate de intretinere si service. | Technical conditions The equipment supplier will provide: - Technical assistance for installation and commissioning. - Installation and operating instructions manual. - Quality certificate. - Free training for the facility staff. - Free service during warranty in authorized maintenance and service workshops.

## F5-61
Nume Proiect / Project Title:Proiectare Si Executie Lucrari Pentru Obiectivul De Investitii: Sediu Nou Pentru Spitalul De Urgenta Prof. Dr. Dimitrie Gerota
Numar Proiect / Project Number: 2S/2024
Data / Date: Septembrie 2025
Beneficiar / Beneficiary: Spitalul de Urgență ”Prof. Dr. Dimitrie Gerota”
Proiectant General / General Designer: Asocierea CCN ALTYAPI YATIRIMLARI VE INSAAT A.S. - CCN YATIRIM HOLDING A.S.
Formular F5: Fisele tehnice pentru echipamente, dotari |  | F5 Form: Technical sheet for equipments, furniture and fixtures
Nr. | Specificatii tehnice impuse prin caietul de sarcini | Technical specifications imposed by specification conditions - techincal notes | Corespondenta propunerii tehnice cu specificatiile tehnice impuse prin caietul de sarcini / Correspondence of the technical proposal with the technical specifications imposed by the specification conditions | Furnizor/Producator Provider/Manufacturer
0 | 1 | 1 | 2 | 3
Fisa tehnica nr. 61 Utilajul, echipamentul tehnologic: Sistem dozare clor - Cod schema W36 |  | Technical sheet no. 61 Machinery, equipment: Chlorine dosing system - Scheme code W36
1 | Parametrii tehnici si functionali Debit minim nominal: 18 mc/h. Sistem complet dozare clor si floculant si control PH: 1. Panou asamblat pentru montre folosit pentru a regla valorile pH-ului, Redox-ului și clorului, cu dozare automată proporțional. Soluția ideală pentru bazine comunale. Vine complet echipat cu sonde, solutie tampon, suport sonda, etc 2. Pompa dozatoare digitala tip TPG Debit constant ajustabil manual sau proportional in functie de un semnal analog extern• Presiune: 0,l- 20 bar • Alimentare: 100÷240 Vac 50-60 Hz • Carcasa: PP armata cu fibra de sticla, grad de protectie IP65 3. Vas stocare chimicale 100 litri Inaltime: 64cm Diametru: 46cm Toata statie se va furniza complet de catre un producator de specialitate Echipamentele statiei de tratare vor fi stabilite in functie de parametrii din buletinul de analiza. | Technical and functional parameters Minimum nominal flow rate: 18 mc/h. Complete system for chlorine and flocculant dosing and PH control: 1. Assembled watch panel used to adjust pH, redox and chlorine values, with automatic proportional dosing. The ideal solution for communal tanks. Comes fully equipped with probes, buffer solution, probe holder, etc 2. Digital dosing pump type TPG Constant flow rate manually adjustable or proportional according to an external analog signal- Pressure: 0,l- 20 bar - Power supply: 100÷240 Vac 50-60 Hz - Housing: PP reinforced with fiberglass, protection degree IP65 3. Chemical storage tank 100 liters Height: 64cm Diameter: 46cm The whole station will be completely supplied by a specialized manufacturer The equipment of the treatment station will be established according to the parameters in the analysis bulletin.
2 | Specificatii de performanta si conditii privind siguranta in exploatare Echipamentele vor fi insotite de cartea tehnica, certificat de calitate si garantie | Performance specifications and operational safety conditions The equipment will be accompanied by the technical manual, certificate of quality, and warranty
3 | Conditii privind conformitatea cu standardele relevante Echipamentul va fi fabricat cf. normelor UE ISO 9001, ISO 14001. | Conditions regarding compliance with relevant standards The equipment shall be built in accordance with EU norms, ISO 9001, ISO 14001.
4 | Conditii de garantie si postgarantie Garantie: minim 2 ani de la punerea in functiune, orice inlocuire a echipamentului in timpul perioadei de garantie va duce la preluarea garantiei de catre echipamentul nou instalat. | Warranty and post-warranty conditions Warranty: minimum 2 years from the time of commissioning, any replacement of the equipment during the warranty period will lead to the warranty being taken over by the newly installed equipment.
5 | Conditii cu caracter tehnic Furnizorul de echipament va oferi: Asistenta tehnica pentru instalare si punere in functiune. Manual de instructiuni pentru instalare si operare. Certificat de calitate. Training gratuit pentru personalul facilitatii. Service gratuit pe perioada garantiei in atelierele autorizate de intretinere si service. | Technical conditions The equipment supplier will provide: - Technical assistance for installation and commissioning. - Installation and operating instructions manual. - Quality certificate. - Free training for the facility staff. - Free service during warranty in authorized maintenance and service workshops.

## F5-63
Nume Proiect / Project Title:Proiectare Si Executie Lucrari Pentru Obiectivul De Investitii: Sediu Nou Pentru Spitalul De Urgenta Prof. Dr. Dimitrie Gerota
Numar Proiect / Project Number: 2S/2024
Data / Date: Septembrie 2025
Beneficiar / Beneficiary: Spitalul de Urgență ”Prof. Dr. Dimitrie Gerota”
Proiectant General / General Designer: Asocierea CCN ALTYAPI YATIRIMLARI VE INSAAT A.S. - CCN YATIRIM HOLDING A.S.
Formular F5: Fisele tehnice pentru echipamente, dotari |  | F5 Form: Technical sheet for equipments, furniture and fixtures
Nr. | Specificatii tehnice impuse prin caietul de sarcini | Technical specifications imposed by specification conditions - techincal notes | Corespondenta propunerii tehnice cu specificatiile tehnice impuse prin caietul de sarcini / Correspondence of the technical proposal with the technical specifications imposed by the specification conditions | Furnizor/Producator Provider/Manufacturer
0 | 1 | 1 | 2 | 3
| Fisa tehnica nr. 63 Utilajul, echipamentul tehnologic:Pompa recirculare bazin put forat - Cod schema W37 | Technical sheet no. 63 Machinery, equipment:Drilled well pool recirculation pump - Scheme code W37
1 | Parametrii tehnici si functionali: Pompa recirculare apa din rezervor (1A), prin racordarea la un rezervor preliminar, echipat cu convertizor de frecventa, compus din o pompa activa. Debit total : 1 l/s; Inaltimea de pompare : 10.00 m Alimentarea : 220 V Pompa este echipat cu: Tablou automatizare general pentru gestionarea functionarii instalatiilor de alimentare cu apa potabila. Complet echipata, inclusiv cablu, tablou automatizare etc Cu agrement de potabilitate | Technical and functional parameters: Pump for recirculation of water from the tank (1A), by connection to a preliminary tank, equipped with a frequency converter, consisting of an active pump. Total flow: 1 l/s; Pumping head: 10.00 m Power supply: 220 V The pump is equipped with: General automation panel for managing the operation of drinking water supply installations. Fully equipped, including cable, automation panel etc. With drinking water approval
2 | Specificatii de performanta si conditii privind siguranta in exploatare: Echipamentele vor fi insotite de cartea tehnica, certificat de calitate si garantie | Performance specifications and operational safety conditions: The equipment will be accompanied by the technical manual, certificate of quality, and warranty
3 | Conditii privind conformitatea cu standardele relevante: Echipamentul va fi fabricat cf. normelor UE, ISO 9001, ISO 14001. | Conditions regarding compliance with relevant standards: The equipment shall be built in accordance with EU norms, ISO 9001, ISO 14001.
4 | Conditii de garantie si postgarantie: Garantie: minim 2 ani de la punerea in functiune, orice inlocuire a echipamentului in timpul perioadei de garantie va duce la preluarea garantiei de catre echipamentul nou instalat. | Warranty and post-warranty conditions Warranty: minimum 2 years from the time of commissioning, any replacement of the equipment during the warranty period will lead to the warranty being taken over by the newly installed equipment.
5 | Conditii cu caracter tehnic: Furnizorul de echipament va oferi: - Asistenta tehnica pentru instalare si punere in functiune. - Manual de instructiuni pentru instalare si operare. - Certificat de calitate. - Training gratuit pentru personalul facilitatii. - Service gratuit pe perioada garantiei in atelierele autorizate de intretinere si service. - Agrement de potabilitate | Technical conditions: The equipment supplier will provide: - Technical assistance for installation and commissioning. - Installation and operating instructions manual. - Quality certificate. - Free training for the facility staff. - Free service during warranty in authorized maintenance and service workshops. - Drinking Water Agrement

## F5-71
#REF!
#REF!
#REF!
#REF!
#REF!
Formular F5: Fisele tehnice pentru echipamente, dotari |  | F5 Form: Technical sheet for equipments, furniture and fixtures
Nr. | Specificatii tehnice impuse prin caietul de sarcini | Technical specifications imposed by specification conditions - techincal notes | Corespondenta propunerii tehnice cu specificatiile tehnice impuse prin caietul de sarcini / Correspondence of the technical proposal with the technical specifications imposed by the specification conditions | Furnizor/Producator Provider/Manufacturer
0 | 1 | 1 | 2 | 3
Fisa tehnica nr. 71 Utilajul, echipamentul tehnologic:Filtru impuritati automat cu sita - Cod schema W35 |  | Technical sheet no. 71 Machinery, equipment: Automatic impurity filter with a screen - Scheme code W35
1 | Parametrii tehnici si functionali Debit minim nominal: 18 mc/h. Diametru racord: Dn100 Limite temperatura apa: 4-48°C Ciclu zile spalare : 1 – 30 zile Sistem de purjare automata, cu sita de inox, manometru, complet echipata Se va furniza cu agrement de potabilitate | Technical and functional parameters Minimum nominal flow rate: 18 m³/h Connection diameter: DN100 Water temperature limits: 4–48°C Backwash cycle interval: 1–30 days Automatic purge system, with stainless steel screen, pressure gauge, fully equipped Supplied with potable water approval certification
2 | Specificatii de performanta si conditii privind siguranta in exploatare Echipamentele vor fi insotite de cartea tehnica, certificat de calitate si garantie | Performance specifications and operational safety conditions The equipment will be accompanied by the technical manual, certificate of quality, and warranty
3 | Conditii privind conformitatea cu standardele relevante Echipamentul va fi fabricat cf. normelor UE ISO 9001, ISO 14001. | Conditions regarding compliance with relevant standards The equipment shall be built in accordance with EU norms, ISO 9001, ISO 14001.
4 | Conditii de garantie si postgarantie Garantie: minim 2 ani de la punerea in functiune, orice inlocuire a echipamentului in timpul perioadei de garantie va duce la preluarea garantiei de catre echipamentul nou instalat. | Warranty and post-warranty conditions Warranty: minimum 2 years from the time of commissioning, any replacement of the equipment during the warranty period will lead to the warranty being taken over by the newly installed equipment.
5 | Conditii cu caracter tehnic Furnizorul de echipament va oferi: Asistenta tehnica pentru instalare si punere in functiune. Manual de instructiuni pentru instalare si operare. Certificat de calitate. Training gratuit pentru personalul facilitatii. Service gratuit pe perioada garantiei in atelierele autorizate de intretinere si service. | Technical conditions The equipment supplier will provide: - Technical assistance for installation and commissioning. - Installation and operating instructions manual. - Quality certificate. - Free training for the facility staff. - Free service during warranty in authorized maintenance and service workshops.